## Summary
Estidama Buildings Energy Prescriptive Pathway v1.0
1 Pearl Compliance
Summary | Envelope | HVAC | SHW | Lighting | Renewables
This tool provides a simple means of demonstrating compliance with the Prescriptive requirements of the Pearl Building Rating System, RE-R1: Minimum Energy Performance credit. This tool forms part of the submittal requirements for the PBRS RE-R1 Prescriptive Method.
Project Info |  |  |  |  | Energy Efficient Appliances Calculator
Project ID |  |  |  |  | Person Responsible
Project Name |  |  |  |  | Company
Location |  |  |  |  | Date of Issue
PQP |  |  |  |  | Mechanical Engineer
Building Type |  | Click to Select |  |  | Electrical Engineer
Total Gross Floor Area, m2 |  |  |  |  | Public Health Engineer
Building Footprint, m2
Building Project Overall Status: |  |  | Fail |  |  |  | Input Cells
Last Revised: April 2011 |  |  |  |  | Report a Template Bug : | PBRS.PrescEnergy@upc.gov.ae |  | Next

## Envelope
Building Envelope
Summary | Envelope | HVAC | SHW | Lighting | Renewables
The following building envelope elements must satisfy the minimum performance requirements where applicable. The quoted Design Value should be an area weighted average of all relevant element types within the project.
| Envelope Element | Construction Type | Included? | Target Requirement | Design Value Achieved | Pass / Fail?
Opaque Elements | Roof U-value, W/m².K |  | No | - |  | PASS
| Wall, above grade U-value, W/m².K |  | No | - |  | PASS
| Wall, Below Grade C-factor, W/m².K | Below grade wall | No | 5.83 |  | PASS
| Floor U-value, W/m².K |  | No | - |  | PASS
| Slab-on-Grade Floor F-factor, W/m.K |  | No | - |  | PASS
Fenestration | Vertical Glazing Area Ratio | Percentage of above grade wall area | No | 30% |  | PASS
| Vertical Glazing U-value, W/m².K |  | No | - |  | PASS
| Vertical Glazing SHGC |  | No | - |  | PASS
| Skylight Glazing Area Ratio | Percentage of roof area | No | 3% |  | PASS
| Skylight Glazing U-value, W/m².K | - | No | 3.8 |  | PASS
| Skylight Glazing SHGC | - | No | 0.3 |  | PASS
Infiltration | Building Air Leakage Rate, l/s/m² | @75Pa Test Pressure | No | 3.64 |  | PASS
Overall Pass / Fail for Building Envelope | [5 empty] | PASS | No
Previous | [6 empty] | Next

## HVAC
HVAC Systems & Controls
Summary |  | Envelope | HVAC | SHW | Lighting | Renewables |  |  | Air conditioners - Air cooled | ac_ac
The following tables consider the performance of various HVAC system components. Compliance must be demonstrated for all mandatory requirements relating to efficiency, fan power and performance. | [8 empty] | Through-the-wall - Air cooled | ttw_ac
|  | Included? | Equipment Type | Size Category | Capacity | Target Requirement | Design Value Achieved | Pass / Fail? | Air conditioners - Water and evaporatively cooled | ac_wec
HVAC Systems | System Efficiency | Unitary Air Conditioners, VRF, Split (& multi-split) units
|  | No |  |  | n/a | 0 |  | PASS | -
[6 empty] | 0 |  | PASS | No
Condensing Units
|  | No |  |  | n/a | 0 |  | PASS | -
[6 empty] | 0 |  | PASS | No
Packaged Terminal Air Conditioners (PTAC) & Packaged Terminal Heat Pumps (PTHP)
|  | No |  | n/a |  | 0 |  | PASS
Air Cooled Chillers
|  | No | Air cooled chiller | n/a |  | 0 |  | PASS
[6 empty] | 0 |  | PASS | No
| System Efficiency Compliance | [6 empty] | PASS | No
| System Fan Power | Fan System Type |  |  | Included? | Target Requirement | Design Value Achieved | Pass / Fail?
|  | Central mechanical ventilation, incl. heating & cooling |  |  | No | 0 |  | PASS
|  | Zonal supply system where fan is remote from zone, i.e. ceiling or roof mounted |  |  | No | 0 |  | PASS
|  | Zonal extract system where fan is remote from zone |  |  | No | 0 |  | PASS
|  | Zonal supply & extract ventilation units such as ceiling void or roof units serving single room/zone with heat recovery |  |  | No | 0 |  | PASS
|  | Local supply & extract ventilation units such as wall/roof units serving single room/zone with heat recovery |  |  | No | 0 |  | PASS
|  | Local supply & extract ventilation units such as window/wall/roof units serving single area (e.g. toilet extract) |  |  | No | 0 |  | PASS
|  | Other local ventilation units |  |  | No | 0 |  | PASS
|  | Fan assisted terminal VAV unit |  |  | No | 0 |  | PASS
|  | Fan coil units (weighted average) |  |  | No | 0 |  | PASS
| System Fan Power Compliance | [6 empty] | PASS | No
| System Performance | Energy Recovery Systems
|  | Is there a dedicated outdoor air system providing fresh air to occupied zones? |  |  | No
|  | Percentage Outdoor Air at Full Design Flow Rate |  |  |  | Please Enter System Airflow Details... |  |  | Yes | n/a
|  | Design Supply Airflow Rate, m³/s |  |  |  | Has an Energy Recovery system been provided? |  | No
[6 empty] | What is the overall effectiveness of the system? (based on change in enthalpy of outdoor air supply) |  |  | PASS
Demand Control Ventilation
|  | Are there any zones with an Occupancy Density exceeding 2.3m²/person? |  |  | No | No Demand Control Ventilation required |  |  | No
|  | Do any of these zones exceed 50m² in area? |  |  | No | Has Demand Control Ventilation been provided? |  | No | PASS
HVAC System Controls
|  | Are individual thermostatic controls provided in each zone, which are capable of responding to temperature within the zone? | [5 empty] | No
|  | Is humidification/dehumidification provided by the system? |  |  | No | Does each humidity control system have associated controls? |  | No
|  | Is the control system a proprietary system? | [5 empty] | No | FAIL
Miscellaneous Additional System Requirements
|  | Are all installed Chilled Water pump motors fitted with Variable Speed Drives? | [5 empty] | n/a | PASS
|  | Are any ducts located in unconditioned spaces? |  |  | No | Are the ducts located in unconditioned spaces insulated with a minimum of R-5 insulation? |  | No | PASS
|  | Are any ducts located in external spaces? |  |  | No | Are the ducts located in external spaces insulated with a minimum of R-8 insulation? |  | No | PASS
|  | Is all piping serving the cooling system insulated with a minimum of 38mm insulation (insulation thermal conductivity < 0.039W/m.K) or equivalent? | [5 empty] | n/a | PASS
| System Performance Compliance | [6 empty] | FAIL
Overall Pass / Fail for HVAC Systems | [7 empty] | FAIL
Previous | [7 empty] | Next

## SHW
Service Hot Water System
Summary | Envelope | HVAC | SHW | Lighting | Renewables
This section considers the performance of the service hot water system, excluding the contribution of any renewable technologies
| Included? | Size Category | Capacity | Target Requirement |  | Design Value Achieved | Pass / Fail?
Electric Hot Water Systems | Hot Water System Efficiency
| No |  |  | 0 |  |  | PASS
Hot Water System Controls
| Are temperature controls provided to satisfy the set point requirements? (43°C for dwellings, 32°C for other occupancies) | [5 empty] | No | PASS
| Are public rest rooms provided? |  | No | Is the hot water outlet temperature limited such that it cannot exceed 43°C? |  |  | No | PASS
| Are swimming pools, spas or hot tubs provided? |  | No | Are the pools equipped with a vapour retardant cover? |  |  | No | PASS
| Are heating or cooling systems provided for swimming pools, spas or hot tubs? |  | No | Is a readily accessible on-off switch provided that can shut off the system without adjusting the thermostat settings? |  |  | No | PASS
| Are any of the swimming pools, spas or hot tubs heated to more than 32°C? |  | No | Are they provided with a cover that has an insulation value exceeding R-12? |  |  | No | PASS
Overall Pass / Fail for SHW Systems | [6 empty] | PASS
Previous | [6 empty] | Next

## Lighting
Lighting
Summary |  | Envelope | HVAC | SHW | Lighting | Renewables
This section considers the overall performance of internal and external lighting systems. Compliance is based upon achievement or improvement beyond the target values outlined in the Abu Dhabi International Energy Conservation Code. Compliance can be demonstrated either for Building Type or on a Space-by-Space basis. Calculation of the lighting power density (W/m²) may require separate calculation relating to lighting power and area of coverage.
Lighting Loads (W/m²)
|  | Building/Space Type |  | Target Requirement | Design Value Achieved | Pass / Fail?
Interior Lighting |  |  |  | - |  | PASS
|  |  |  | - |  | PASS
|  |  |  | - |  | PASS
|  |  |  | - |  | PASS
|  |  |  | - |  | PASS
|  |  |  | - |  | PASS
|  |  |  | - |  | PASS
|  |  |  | - |  | PASS
|  |  |  | - |  | PASS
|  |  |  | - |  | PASS
|  |  |  | - |  | PASS
|  |  |  | - |  | PASS
|  |  |  | - |  | PASS
|  |  |  | - |  | PASS
|  |  |  | - |  | PASS
|  |  |  | - |  | PASS
|  |  |  | - |  | PASS
|  |  |  | - |  | PASS
|  |  |  | - |  | PASS
|  |  |  | - |  | PASS
Overall Pass / Fail for Internal Lighting | [5 empty] | PASS | No
Is Exterior Lighting Provided? |  |  |  | No | Lighting Loads
|  | Area Type | Units | Included? | Target Requirement | Design Value Achieved | Length/Area | Pass / Fail? |  | Target Check | Design Check | Info Check | Inclusion Check
Exterior Lighting | Tradable Surfaces | Parking Lots and Drives | W/m² | No | 1.45 |  |  | n/a |  | 0 | 0 | No | No
|  | Walkways <3m Wide | W/linear meter | No | 2.95 |  |  |  |  | 0 | 0 | No | No
|  | Walkways ≥3m Wide | W/linear meter | No | 1.94 |  |  |  |  | 0 | 0 | No | No
|  | Stairways | W/m² | No | 9.69 |  |  |  |  | 0 | 0 | No | No
|  | Main Entrance Door | W/linear m of door width | No | 88.6 |  |  |  |  | 0 | 0 | No | No
|  | Other Entrance Doors | W/linear m of door width | No | 59.1 |  |  |  |  | 0 | 0 | No | No
|  | Canopies and Overhangs | W/m² | No | 12.1 |  |  |  |  | 0 | 0 | No | No
|  | Outdoor Sales, Open Areas | W/m² | No | 4.84 |  |  |  |  | 0 | 0 | No | No
|  | Outdoor Sales, Street Frontage | W/linear meter | No | 59.1 |  |  |  |  | 0 | 0 | No | No
| Tradable Surfaces Compliance | [6 empty] | PASS | No | 0 | 0 | 0 | 0
| Non-Tradable Surfaces | Building Façade | W/m² for each illuminated wall or surface | No | - |  |  | PASS
|  | Automated teller machines and night depositories | W per location | No | 243 |  |  | PASS
|  |  | W per additional ATM per location | No | 81 |  |  | PASS
|  | Inspection stations at guarded facilities | W/m² of uncovered area | No | 12.1094 |  |  | PASS
|  | Loading areas emergency service vehicles | W/m² of uncovered area | No | 4.8438 |  |  | PASS
|  | Drive-up windows at fast food restaurants | W per drive-through | No | 360 |  |  | PASS
|  | Parking near 24-hour retail entrances | W per main entry | No | 720 |  |  | PASS
Overall Pass / Fail for External Lighting | [7 empty] | PASS | No
Previous | [7 empty] | Next

## Renewables
Renewable Energy
Summary | Envelope | HVAC | SHW | Lighting | Renewables
This section considers the provision of an adequate solar thermal system for office buildings. For other building typologies there is no requirement to provide renewable technologies.
|  | Included? | Total Building Predicted Load | Target Requirement, kWh | Achieved, kWh | Pass / Fail?
Total Yearly Hot Water Usage Generated from Renewable Sources (kWh) |  | No |  | 0 |  | n/a
Overall Pass / Fail for Renewables | [5 empty] | PASS | No
Previous

## Reference (hidden)
Building Envelope |  |  | HVAC | [8 empty] | SHW |  |  |  | Lighting
Opaque Elements |  |  | System Efficiencies | [8 empty] | System Efficiencies |  |  |  | Interior Power Densities
| General | "Residential" | UNITARY AIR CONDITIONERS AND CONDENSING UNITS, ELECTRICALLY OPERATED | [8 empty] | Size Category (Input) | Subcategory or Rating Condition | Minimum Efficiency | Test Procedure |  | Whole Building | Space by Space | Returned Values
Roof: |  |  |  | Equipment Type | Size Category | Minimum Efficiency | [5 empty] | < 12 kW | Resistance | 0.97 - 0.000349V, EF | DOE 10 CFR Part 430
Insulation entirely above deck | 0.2 | 0.2 |  | Air conditioners, Air cooled | < 19kW | 13.0 SEER | 3.81 SCoP |  |  |  |  | > 12 kW | Resistance | 0.134V + 45.4 SL, W | ANSI Z21.10.3 | Active Storage |  | 7.75 | 7.75
Metal buildings | 0.33 | 0.33 |  |  | > 19kW and < 40kW | 11.2 EER | 3.28 CoP |  |  |  |  | < 24 amps and < 250 volts | Heat pump | 0.97 - 0.000349V, EF | DOE 10 CFR Part 430 | Atrium – First Three Floors |  | 5.8125 | 5.8125
Attic and other | 0.17 | 0.14 |  |  | > 40kW and < 70kW | 11.0 EER | 3.22 CoP | [8 empty] | Atrium – Each Additional Floor |  | 1.9375 | 1.9375
Wall, Above Grade: |  |  |  |  | > 70kW and < 223kW | 10.0 EER | 2.93 CoP | 9.7 IPLV | [7 empty] | AUTOMOTIVE FACILITY | 8.7188 |  | 8.7188
Mass | 0.3 | 0.3 |  |  | > 223kW | 9.7 EER | 2.84 CoP | 9.4 IPLV | [7 empty] | Classroom/lecture/training |  | 12.5938 | 12.5938
Metal buildings | 0.48 | 0.48 |  | Through-the-wall, Air cooled | < 9kW | 12.0 SEER | 3.52 SCoP | [8 empty] | Conference/Meeting/Multipurpose |  | 10.6563 | 10.6563
Metal framed | 0.19 | 0.19 |  | Air conditioners, Water and evaporatively cooled | < 19kW | 12.1 EER | 3.55 CoP | [8 empty] | Corridor/Transition |  | 4.8438 | 4.8438
Wood framed and other | 0.18 | 0.18 |  |  | > 19kW and < 40kW | 11.5 EER | 3.37 CoP | [8 empty] | Electrical/Mechanical |  | 10.6563 | 10.6563
Wall, Below Grade C-factor, W/m².K: |  |  |  |  | > 40kW and < 70kW | 11.0 EER | 3.22 CoP | [8 empty] | Food Preparation |  | 11.625 | 11.625
Below grade wall | 5.83 | 5.83 |  |  | > 70kW and < 223kW | 11.5 EER | 3.37 CoP | [8 empty] | Inactive Storage |  | 1.9375 | 1.9375
Floors U-value, W/m2.K: |  |  | UNITARY AIR CONDITIONERS AND CONDENSING UNITS, ELECTRICALLY OPERATED | [12 empty] | Lobby |  | 10.6563 | 10.6563
Mass | 1.65 | 1.65 |  | Equipment Type | Size Category | Minimum Efficiency | [9 empty] | Restroom |  | 7.75 | 7.75
Joist/Framing | 1.44 | 1.44 |  | Air cooled,(Cooling mode) | < 19kW | 13.0 SEER | 3.81 SCoP | [8 empty] | Stairway |  | 5.8125 | 5.8125
Slab-on-Grade Floors F-factor, W/m.K: |  |  |  |  | > 19kW and < 40kW | 11.0 EER | 3.22 CoP | [8 empty] | CONVENTION CENTER | 11.625 |  | 11.625
Unheated slabs (F) | 3.73 | 3.73 |  |  | > 40kW and < 70kW | 10.6 EER | 3.11 CoP | [8 empty] | Exhibit Space |  | 12.5938 | 12.5938
Heated slabs (F) | 5.21 | 5.21 |  |  | > 70kW | 9.5 EER | 2.78 CoP | 9.2 IPLV | [7 empty] | Audience/Seating Area |  | 8.7188 | 8.7188
|  |  |  | Through-the-Wall (Air cooled, cooling mode) | < 9kW | 12.0 SEER | 3.52 SCoP | [8 empty] | COURTHOUSE | 11.625 |  | 11.625
Fenestration |  |  | PACKAGED TERMINAL AIR CONDITIONERS AND PACKAGED TERMINAL HEAT PUMPS | [12 empty] | Audience/Seating Area |  | 8.7188 | 8.7188
Vertical Glazing (Max 30% above grade wall area) |  |  |  | Equipment Type | Size Category (Input) | Subcategory or Rating Condition | Minimum Efficiency | [8 empty] | Courtroom |  | 18.4063 | 18.4063
Non-metal | 2 |  |  | PTAC (Cooling mode) | All capacities | 95ºF db outdoor air | 12.5 - (0.213 * Cap/1000) EER | [8 empty] | Confinement Cells |  | 8.7188 | 8.7188
Curtain wall/storefront | 1.9 |  |  | PTHP (Cooling mode) | All capacities | 95ºF db outdoor air | 12.5 - (0.213 * Cap/1000) EER | [8 empty] | Judges Chambers |  | 12.5938 | 12.5938
Entrance door | 2.6 |  | WATER CHILLING PACKAGES | [12 empty] | Dressing/Locker/Fitting Room |  | 5.8125 | 5.8125
All other | 1.9 |  |  | Equipment Type | Size Category | Minimum Efficiency | [9 empty] | DINING: BAR LOUNGE/LEISURE | 12.5938 |  | 12.5938
SHGC all frame types | [5 empty] | Full Load, EER | Full Load, CoP | IPLV | [7 empty] | Lounge/Leisure Dining |  | 13.5625 | 13.5625
PF < 0.25 | 0.225 |  |  | Air-cooled chillers | < 150 tons | > 9.562 | > 2.803 | > 12.500 | [7 empty] | DINING: CAFETERIA/FAST FOOD | 13.5625 |  | 13.5625
0.25 ≤ PF < 0.50 | 0.297 |  |  |  | > 150 tons | > 9.562 | > 2.803 | > 12.750 | [7 empty] | DINING: FAMILY | 15.5 |  | 15.5
PF ≥ 0.50 | 0.36 |  |  | Air cooled without condenser, electrical operated | All capacities | Air-cooled chillers without condensers must be rated with matching condensers and comply with the air-cooled chiller efficiency requirements | [9 empty] | Dining |  | 13.5625 | 13.5625
[16 empty] | Kitchen |  | 11.625 | 11.625
Skylight (Max 3% roof area) |  |  | Energy Recovery Systems | [12 empty] | DORMITORY | 9.6875 |  | 9.6875
U-value (W/m².K) | 3.8 |  |  | Percentage Outdoor Air at Full Design Flow Rate |  | >30% &<40% | >40% & <50% | >50% & <60% | >60% & <70% | >70% & <80% | >80% |  |  |  |  | Living Quarters |  | 10.6563 | 10.6563
SHGC | 0.3 |  |  | Design Supply Fan Airflow Rate | m³/s | n/a | n/a | 11.0436 | 5.097 | 2.1238 | 1.699 |  |  |  |  | Bedroom |  | 4.8438 | 4.8438
[16 empty] | Study Hall |  | 13.5625 | 13.5625
|  |  | Maximum specific fan powers in air distribution systems in new buildings | [12 empty] | EXERCISE CENTER | 9.6875 |  | 9.6875
|  |  |  | System Type | SFP, W/l/s | [10 empty] | Dressing/Locker/Fitting Room |  | 5.8125 | 5.8125
|  |  |  | Central mechanical ventilation, incl. heating & cooling | 1.8 | [10 empty] | Audience/Seating Area |  | 2.9063 | 2.9063
|  |  |  | Zonal supply system where fan is remote from zone, i.e. ceiling or roof mounted | 1.2 | [10 empty] | Exercise Area |  | 8.7188 | 8.7188
|  |  |  | Zonal extract system where fan is remote from zone | 0.6 | [10 empty] | Exercise Area/Gymnasium |  | 8.7188 | 8.7188
|  |  |  | Zonal supply & extract ventilation units such as ceiling void or roof units serving single room/zone with heat recovery | 2 | [10 empty] | GYMNASIUM | 10.6563 |  | 10.6563
|  |  |  | Local supply & extract ventilation units such as wall/roof units serving single room/zone with heat recovery | 1.8 | [10 empty] | Dressing/Locker/Fitting Room |  | 5.8125 | 5.8125
|  |  |  | Local supply & extract ventilation units such as window/wall/roof units serving single area (e.g. toilet extract) | 0.4 | [10 empty] | Audience/Seating Area |  | 3.875 | 3.875
|  |  |  | Other local ventilation units | 0.6 | [10 empty] | Playing Area |  | 13.5625 | 13.5625
|  |  |  | Fan assisted terminal VAV unit | 1.2 | [10 empty] | Exercise Area |  | 8.7188 | 8.7188
|  |  |  | Fan coil units (weighted average) | 0.6 | [10 empty] | HEALTHCARE CLINIC | 9.6875 |  | 9.6875
[16 empty] | Corridors w/patient waiting, exam |  | 9.6875 | 9.6875
[16 empty] | Exam/Treatment |  | 14.5313 | 14.5313
[16 empty] | Emergency |  | 26.1563 | 26.1563
[16 empty] | Public & Staff Lounge |  | 7.75 | 7.75
[16 empty] | Hospital/Medical supplies |  | 13.5625 | 13.5625
[16 empty] | Hospital - Nursery |  | 5.8125 | 5.8125
[16 empty] | Nurse station |  | 9.6875 | 9.6875
[16 empty] | Physical therapy |  | 8.7188 | 8.7188
[16 empty] | Patient Room |  | 6.7813 | 6.7813
[16 empty] | Pharmacy |  | 11.625 | 11.625
[16 empty] | Hospital/Radiology |  | 3.875 | 3.875
[16 empty] | Operating Room |  | 21.3125 | 21.3125
[16 empty] | Recovery |  | 7.75 | 7.75
[16 empty] | Active storage |  | 8.7188 | 8.7188
[16 empty] | Laundry-Washing |  | 5.8125 | 5.8125
[16 empty] | HOTEL | 9.6875 |  | 9.6875
[16 empty] | Dining Area |  | 12.5938 | 12.5938
[16 empty] | Guest quarters |  | 10.6563 | 10.6563
[16 empty] | Reception/Waiting |  | 24.2188 | 24.2188
[16 empty] | Lobby |  | 10.6563 | 10.6563
[16 empty] | LIBRARY | 12.5938 |  | 12.5938
[16 empty] | Library-Audio Visual |  | 6.7813 | 6.7813
[16 empty] | Stacks |  | 16.4688 | 16.4688
[16 empty] | Card File & Cataloguing |  | 10.6563 | 10.6563
[16 empty] | Reading Area |  | 11.625 | 11.625
[16 empty] | MANUFACTURING FACILITY | 12.5938 |  | 12.5938
[16 empty] | MOTEL | 9.6875 |  | 9.6875
[16 empty] | Dining Area |  | 11.625 | 11.625
[16 empty] | Guest quarters |  | 10.6563 | 10.6563
[16 empty] | Reception/Waiting |  | 20.3438 | 20.3438
[16 empty] | MOTION PICTURE THEATER | 11.625 |  | 11.625
[16 empty] | Audience/Seating Area |  | 11.625 | 11.625
[16 empty] | Lobby |  | 9.6875 | 9.6875
[16 empty] | MULTI-FAMILY | 6.7813 |  | 6.7813
[16 empty] | MUSEUM | 10.6563 |  | 10.6563
[16 empty] | Active Storage |  | 7.75 | 7.75
[16 empty] | General exhibition |  | 9.6875 | 9.6875
[16 empty] | Restoration |  | 16.4688 | 16.4688
[16 empty] | OFFICE | 8.7188 |  | 8.7188
[16 empty] | Enclosed |  | 9.6875 | 9.6875
[16 empty] | Open Plan |  | 9.6875 | 9.6875
[16 empty] | PARKING GARAGE | 2.9063 |  | 2.9063
[16 empty] | PENITENTIARY | 9.6875 |  | 9.6875
[16 empty] | PERFORMING ARTS THEATER | 15.5 |  | 15.5
[16 empty] | Audience/Seating Area |  | 25.1875 | 25.1875
[16 empty] | Lobby |  | 31.9688 | 31.9688
[16 empty] | Dressing/Locker/Fitting Room |  | 10.6563 | 10.6563
[16 empty] | POLICE STATIONS | 9.6875 |  | 9.6875
[16 empty] | FIRE STATIONS | 7.75 |  | 7.75
[16 empty] | Fire Station Engine Room |  | 7.75 | 7.75
[16 empty] | Sleeping Quarters |  | 2.9063 | 2.9063
[16 empty] | Audience/Seating Area |  | 7.75 | 7.75
[16 empty] | Police Station Laboratory |  | 13.5625 | 13.5625
[16 empty] | POST OFFICE/SF | 10.6563 |  | 10.6563
[16 empty] | Sorting Area |  | 11.625 | 11.625
[16 empty] | Lobby |  | 9.6875 | 9.6875
[16 empty] | RELIGIOUS BUILDINGS | 12.5938 |  | 12.5938
[16 empty] | Lobby |  | 5.8125 | 5.8125
[16 empty] | Worship/Pulpit/Choir |  | 23.25 | 23.25
[16 empty] | RETAIL | 12.5938 |  | 12.5938
[16 empty] | Department Store Sales Area |  | 12.5938 | 12.5938
[16 empty] | Specialty Store Sales Area |  | 17.4375 | 17.4375
[16 empty] | Fine Merchandise Sales Area |  | 28.0938 | 28.0938
[16 empty] | Supermarket Sales Area |  | 12.5938 | 12.5938
[16 empty] | Personal Services Sales Area |  | 12.5938 | 12.5938
[16 empty] | Mass Merchandising Sales Area |  | 12.5938 | 12.5938
[16 empty] | Mall Concourse |  | 16.4688 | 16.4688
[16 empty] | RETAIL: SPECIALTY | 15.5 |  | 15.5
[16 empty] | RETAIL: SUPERMARKET | 12.5938 |  | 12.5938
[16 empty] | SCHOOL/UNIVERSITY | 11.625 |  | 11.625
[16 empty] | Classroom |  | 12.5938 | 12.5938
[16 empty] | Audience |  | 6.7813 | 6.7813
[16 empty] | Dining |  | 10.6563 | 10.6563
[16 empty] | Office |  | 10.6563 | 10.6563
[16 empty] | Corridor |  | 4.8438 | 4.8438
[16 empty] | Storage |  | 4.8438 | 4.8438
[16 empty] | Laboratory |  | 10.6563 | 10.6563
[16 empty] | TOWN HALL | 10.6563 |  | 10.6563
[16 empty] | TRANSPORTATION | 9.6875 |  | 9.6875
[16 empty] | Dining Area |  | 20.3438 | 20.3438
[16 empty] | Baggage Area |  | 9.6875 | 9.6875
[16 empty] | Airport - Concourse |  | 5.8125 | 5.8125
[16 empty] | Terminal - Ticket Counter |  | 14.5313 | 14.5313
[16 empty] | Reception/Waiting |  | 4.8438 | 4.8438
[16 empty] | SPORTS ARENA | 10.6563 |  | 10.6563
[16 empty] | WAREHOUSE | 5.8125 |  | 5.8125
[16 empty] | Fine Material |  | 13.5625 | 13.5625
[16 empty] | Medium/Bulky Material |  | 5.8125 | 5.8125
[16 empty] | WORKSHOP | 13.5625 |  | 13.5625